## Caso_Base
Análisis | Variable | Run_Caso_Base | Valor_Caso_Base | EUI_kWh/m2_Caso_Base | Gas_MWh | Elec_MWh | Gas_kWh/m2 | Elec_kWh/m2 | EUI_kWh/m2 | CE_kgCO2/m2 | UK_BER_kgCO2/m2 | Ta_max_degC | Boiler_max_kW | Chiller_max_kW | DHW_heating_kWh/m2 | Space_heating_(gas)_kWh/m2 | Space_heating_(elec)_kWh/m2 | Space_cooling_kWh/m2
computergain | computer_gain | 0 | Equipment1 | 225.61 | 0 | 6168.16 | 0 | 231.23 | 225.61 | 117.09 | 0 | 66.71 | 52.25 | 0.13 | 26.01 | 0 | 8.28 | 43.7
dhwlphperperson | dhw_lph_per_person | 0 | 0.4 | 225.61 | 0 | 6168.15 | 0 | 231.23 | 225.61 | 117.09 | 0 | 66.71 | 52.25 | 0.13 | 26.01 | 0 | 8.28 | 43.7
genlightinggain | gen_lighting_gain | 0 | Lighting1 | 225.61 | 0 | 6168.15 | 0 | 231.23 | 225.61 | 117.09 | 0 | 66.71 | 52.25 | 0.13 | 26.01 | 0 | 8.28 | 43.7
peoplem2perperson | people_m2_per_person | 0 | 8.6 | 225.61 | 0 | 6168.15 | 0 | 231.23 | 225.61 | 117.09 | 0 | 66.71 | 52.25 | 0.13 | 26.01 | 0 | 8.28 | 43.7

## computergain
Run | Variable | Valor | Dif_VS_Caso_Base | %_Cambio | EUI_kWh/m2_Caso_Base | EUI_kWh/m2_Run_0 | EUI_kWh/m2_Cambio | EUI_kWh/m2_%_Cambio | Elec_kWh/m2_Caso_Base | Elec_kWh/m2_Run_0 | Elec_kWh/m2_Cambio | Elec_kWh/m2_%_Cambio | Gas_kWh/m2_Caso_Base | Gas_kWh/m2_Run_0 | Gas_kWh/m2_Cambio | Gas_kWh/m2_%_Cambio | CE_kgCO2/m2_Caso_Base | CE_kgCO2/m2_Run_0 | CE_kgCO2/m2_Cambio | CE_kgCO2/m2_%_Cambio | DHW_heating_kWh/m2_Caso_Base | DHW_heating_kWh/m2_Run_0 | DHW_heating_kWh/m2_Cambio | DHW_heating_kWh/m2_%_Cambio | EUI_kWh/m2_Run_1 | Elec_kWh/m2_Run_1 | Gas_kWh/m2_Run_1 | CE_kgCO2/m2_Run_1 | DHW_heating_kWh/m2_Run_1 | EUI_kWh/m2_Run_2 | Elec_kWh/m2_Run_2 | Gas_kWh/m2_Run_2 | CE_kgCO2/m2_Run_2 | DHW_heating_kWh/m2_Run_2
0 | computer_gain | Equipment1 | N/A | N/A | 225.61 | 225.61 | 0 | 0 | 231.23 | 231.23 | 0 | 0 | 0 | 0 | 0 | 0 | 117.09 | 117.09 | 0 | 0 | 26.01 | 26.01 | 0 | 0
1 | computer_gain | Equipment2 | N/A | N/A | 225.61 |  | -42.65 | -18.9043 | 231.23 |  | -42.64 | -18.4405 | 0 |  | 0 | 0 | 117.09 |  | -22.13 | -18.9 | 26.01 |  | 0 | 0 | 182.96 | 188.59 | 0 | 94.96 | 26.01
2 | computer_gain | Equipment3 | N/A | N/A | 225.61 |  | 14.57 | 6.458 | 231.23 |  | 14.57 | 6.3011 | 0 |  | 0 | 0 | 117.09 |  | 7.56 | 6.4566 | 26.01 |  | 0 | 0 | [5 empty] | 240.18 | 245.8 | 0 | 124.65 | 26.01

## dhwlphperperson
Run | Variable | Valor | Dif_VS_Caso_Base | %_Cambio | EUI_kWh/m2_Caso_Base | EUI_kWh/m2_Run_0 | EUI_kWh/m2_Cambio | EUI_kWh/m2_%_Cambio | Elec_kWh/m2_Caso_Base | Elec_kWh/m2_Run_0 | Elec_kWh/m2_Cambio | Elec_kWh/m2_%_Cambio | Gas_kWh/m2_Caso_Base | Gas_kWh/m2_Run_0 | Gas_kWh/m2_Cambio | Gas_kWh/m2_%_Cambio | CE_kgCO2/m2_Caso_Base | CE_kgCO2/m2_Run_0 | CE_kgCO2/m2_Cambio | CE_kgCO2/m2_%_Cambio | DHW_heating_kWh/m2_Caso_Base | DHW_heating_kWh/m2_Run_0 | DHW_heating_kWh/m2_Cambio | DHW_heating_kWh/m2_%_Cambio | EUI_kWh/m2_Run_1 | Elec_kWh/m2_Run_1 | Gas_kWh/m2_Run_1 | CE_kgCO2/m2_Run_1 | DHW_heating_kWh/m2_Run_1 | EUI_kWh/m2_Run_2 | Elec_kWh/m2_Run_2 | Gas_kWh/m2_Run_2 | CE_kgCO2/m2_Run_2 | DHW_heating_kWh/m2_Run_2
0 | dhw_lph_per_person | 0.4 | 0 | 0 | 225.61 | 225.61 | 0 | 0 | 231.23 | 231.23 | 0 | 0 | 0 | 0 | 0 | 0 | 117.09 | 117.09 | 0 | 0 | 26.01 | 26.01 | 0 | 0
1 | dhw_lph_per_person | 0.7 | 0.3 | 75 | 225.61 |  | 19.51 | 8.6477 | 231.23 |  | 19.51 | 8.4375 | 0 |  | 0 | 0 | 117.09 |  | 10.13 | 8.6515 | 26.01 |  | 19.52 | 75.0481 | 245.12 | 250.74 | 0 | 127.22 | 45.53
2 | dhw_lph_per_person | 0.2 | -0.2 | -50 | 225.61 |  | -13.01 | -5.7666 | 231.23 |  | -13 | -5.6221 | 0 |  | 0 | 0 | 117.09 |  | -6.75 | -5.7648 | 26.01 |  | -13 | -49.9808 | [5 empty] | 212.6 | 218.23 | 0 | 110.34 | 13.01

## genlightinggain
Run | Variable | Valor | Dif_VS_Caso_Base | %_Cambio | EUI_kWh/m2_Caso_Base | EUI_kWh/m2_Run_0 | EUI_kWh/m2_Cambio | EUI_kWh/m2_%_Cambio | Elec_kWh/m2_Caso_Base | Elec_kWh/m2_Run_0 | Elec_kWh/m2_Cambio | Elec_kWh/m2_%_Cambio | Gas_kWh/m2_Caso_Base | Gas_kWh/m2_Run_0 | Gas_kWh/m2_Cambio | Gas_kWh/m2_%_Cambio | CE_kgCO2/m2_Caso_Base | CE_kgCO2/m2_Run_0 | CE_kgCO2/m2_Cambio | CE_kgCO2/m2_%_Cambio | DHW_heating_kWh/m2_Caso_Base | DHW_heating_kWh/m2_Run_0 | DHW_heating_kWh/m2_Cambio | DHW_heating_kWh/m2_%_Cambio | EUI_kWh/m2_Run_1 | Elec_kWh/m2_Run_1 | Gas_kWh/m2_Run_1 | CE_kgCO2/m2_Run_1 | DHW_heating_kWh/m2_Run_1 | EUI_kWh/m2_Run_2 | Elec_kWh/m2_Run_2 | Gas_kWh/m2_Run_2 | CE_kgCO2/m2_Run_2 | DHW_heating_kWh/m2_Run_2
0 | gen_lighting_gain | Lighting1 | N/A | N/A | 225.61 | 225.61 | 0 | 0 | 231.23 | 231.23 | 0 | 0 | 0 | 0 | 0 | 0 | 117.09 | 117.09 | 0 | 0 | 26.01 | 26.01 | 0 | 0
1 | gen_lighting_gain | Lighting2 | N/A | N/A | 225.61 |  | -3.51 | -1.5558 | 231.23 |  | -3.51 | -1.518 | 0 |  | 0 | 0 | 117.09 |  | -1.82 | -1.5544 | 26.01 |  | 0 | 0 | 222.1 | 227.72 | 0 | 115.27 | 26.01
2 | gen_lighting_gain | Lighting3 | N/A | N/A | 225.61 |  | 7.37 | 3.2667 | 231.23 |  | 7.37 | 3.1873 | 0 |  | 0 | 0 | 117.09 |  | 3.83 | 3.271 | 26.01 |  | 0 | 0 | [5 empty] | 232.98 | 238.6 | 0 | 120.92 | 26.01

## peoplem2perperson
Run | Variable | Valor | Dif_VS_Caso_Base | %_Cambio | EUI_kWh/m2_Caso_Base | EUI_kWh/m2_Run_0 | EUI_kWh/m2_Cambio | EUI_kWh/m2_%_Cambio | Elec_kWh/m2_Caso_Base | Elec_kWh/m2_Run_0 | Elec_kWh/m2_Cambio | Elec_kWh/m2_%_Cambio | Gas_kWh/m2_Caso_Base | Gas_kWh/m2_Run_0 | Gas_kWh/m2_Cambio | Gas_kWh/m2_%_Cambio | CE_kgCO2/m2_Caso_Base | CE_kgCO2/m2_Run_0 | CE_kgCO2/m2_Cambio | CE_kgCO2/m2_%_Cambio | DHW_heating_kWh/m2_Caso_Base | DHW_heating_kWh/m2_Run_0 | DHW_heating_kWh/m2_Cambio | DHW_heating_kWh/m2_%_Cambio | EUI_kWh/m2_Run_1 | Elec_kWh/m2_Run_1 | Gas_kWh/m2_Run_1 | CE_kgCO2/m2_Run_1 | DHW_heating_kWh/m2_Run_1 | EUI_kWh/m2_Run_2 | Elec_kWh/m2_Run_2 | Gas_kWh/m2_Run_2 | CE_kgCO2/m2_Run_2 | DHW_heating_kWh/m2_Run_2
0 | people_m2_per_person | 8.6 | 0 | 0 | 225.61 | 225.61 | 0 | 0 | 231.23 | 231.23 | 0 | 0 | 0 | 0 | 0 | 0 | 117.09 | 117.09 | 0 | 0 | 26.01 | 26.01 | 0 | 0
1 | people_m2_per_person | 17.24 | 8.64 | 100.4651 | 225.61 |  | -16.05 | -7.114 | 231.23 |  | -16.04 | -6.9368 | 0 |  | 0 | 0 | 117.09 |  | -8.33 | -7.1142 | 26.01 |  | -13.04 | -50.1346 | 209.56 | 215.19 | 0 | 108.76 | 12.97
2 | people_m2_per_person | 5.75 | -2.85 | -33.1395 | 225.61 |  | 16.72 | 7.411 | 231.23 |  | 16.72 | 7.2309 | 0 |  | 0 | 0 | 117.09 |  | 8.68 | 7.4131 | 26.01 |  | 12.89 | 49.5579 | [5 empty] | 242.33 | 247.95 | 0 | 125.77 | 38.9

## Datos_computergain
run | computer_gain | Gas_MWh | Elec_MWh | Gas_kWh/m2 | Elec_kWh/m2 | Boilers_MWh | Chillers_MWh | Boilers_kWh/m2 | Chillers_kWh/m2 | CE_kgCO2/m2 | UK_BER_kgCO2/m2 | EUI_kWh/m2 | Ta_max_degC | Boiler_max_kW | Chiller_max_kW | Interior_lighting_kWh/m2 | Exterior_lighting_kWh/m2 | Space_heating_(gas)_kWh/m2 | Space_heating_(elec)_kWh/m2 | Space_cooling_kWh/m2 | Pumps_kWh/m2 | Fans_interior_kWh/m2 | DHW_heating_kWh/m2 | Receptacle_equipment_kWh/m2 | Elevators_escalators_kWh/m2 | Data_center_equipment_kWh/m2 | Cooking_(gas)_kWh/m2 | Cooking_(elec)_kWh/m2 | Refrigeration_kWh/m2 | Wind_PV_kWh/m2
0 | Equipment1 | 0 | 6168.16 | 0 | 231.23 | 171.66 | 0 | 6.44 | 0 | 117.09 | 0 | 225.61 | 66.71 | 52.25 | 0.13 | 22.04 | 0.6 | 0 | 8.28 | 43.7 | 0 | 11.3 | 26.01 | 99.42 | 11.82 | 0 | 0 | 0 | 0 | -5.62
1 | Equipment2 | 0 | 5030.51 | 0 | 188.59 | 171.66 | 0 | 6.44 | 0 | 94.96 | 0 | 182.96 | 66.51 | 52.25 | 0.03 | 22.04 | 0.6 | 0 | 18.72 | 30.56 | 0 | 11.17 | 26.01 | 60.44 | 11.82 | 0 | 0 | 0 | 0 | -5.62
2 | Equipment3 | 0 | 6556.76 | 0 | 245.8 | 171.66 | 0 | 6.44 | 0 | 124.65 | 0 | 240.18 | 66.77 | 52.25 | 0.15 | 22.04 | 0.6 | 0 | 7.91 | 47.39 | 0 | 11.57 | 26.01 | 110.16 | 11.82 | 0 | 0 | 0 | 0 | -5.62

## Datos_dhwlphperperson
run | dhw_lph_per_person | Gas_MWh | Elec_MWh | Gas_kWh/m2 | Elec_kWh/m2 | Boilers_MWh | Chillers_MWh | Boilers_kWh/m2 | Chillers_kWh/m2 | CE_kgCO2/m2 | UK_BER_kgCO2/m2 | EUI_kWh/m2 | Ta_max_degC | Boiler_max_kW | Chiller_max_kW | Interior_lighting_kWh/m2 | Exterior_lighting_kWh/m2 | Space_heating_(gas)_kWh/m2 | Space_heating_(elec)_kWh/m2 | Space_cooling_kWh/m2 | Pumps_kWh/m2 | Fans_interior_kWh/m2 | DHW_heating_kWh/m2 | Receptacle_equipment_kWh/m2 | Elevators_escalators_kWh/m2 | Data_center_equipment_kWh/m2 | Cooking_(gas)_kWh/m2 | Cooking_(elec)_kWh/m2 | Refrigeration_kWh/m2 | Wind_PV_kWh/m2
0 | 0.4 | 0 | 6168.15 | 0 | 231.23 | 171.66 | 0 | 6.44 | 0 | 117.09 | 0 | 225.61 | 66.71 | 52.25 | 0.13 | 22.04 | 0.6 | 0 | 8.28 | 43.7 | 0 | 11.3 | 26.01 | 99.42 | 11.82 | 0 | 0 | 0 | 0 | -5.62
1 | 0.7 | 0 | 6688.6 | 0 | 250.74 | 300.4 | 0 | 11.26 | 0 | 127.22 | 0 | 245.12 | 66.71 | 91.45 | 0.13 | 22.04 | 0.6 | 0 | 8.28 | 43.7 | 0 | 11.3 | 45.53 | 99.42 | 11.82 | 0 | 0 | 0 | 0 | -5.62
2 | 0.2 | 0 | 5821.19 | 0 | 218.23 | 85.83 | 0 | 3.22 | 0 | 110.34 | 0 | 212.6 | 66.71 | 26.13 | 0.13 | 22.04 | 0.6 | 0 | 8.28 | 43.7 | 0 | 11.3 | 13.01 | 99.42 | 11.82 | 0 | 0 | 0 | 0 | -5.62

## Datos_genlightinggain
run | gen_lighting_gain | Gas_MWh | Elec_MWh | Gas_kWh/m2 | Elec_kWh/m2 | Boilers_MWh | Chillers_MWh | Boilers_kWh/m2 | Chillers_kWh/m2 | CE_kgCO2/m2 | UK_BER_kgCO2/m2 | EUI_kWh/m2 | Ta_max_degC | Boiler_max_kW | Chiller_max_kW | Interior_lighting_kWh/m2 | Exterior_lighting_kWh/m2 | Space_heating_(gas)_kWh/m2 | Space_heating_(elec)_kWh/m2 | Space_cooling_kWh/m2 | Pumps_kWh/m2 | Fans_interior_kWh/m2 | DHW_heating_kWh/m2 | Receptacle_equipment_kWh/m2 | Elevators_escalators_kWh/m2 | Data_center_equipment_kWh/m2 | Cooking_(gas)_kWh/m2 | Cooking_(elec)_kWh/m2 | Refrigeration_kWh/m2 | Wind_PV_kWh/m2
0 | Lighting1 | 0 | 6168.15 | 0 | 231.23 | 171.66 | 0 | 6.44 | 0 | 117.09 | 0 | 225.61 | 66.71 | 52.25 | 0.13 | 22.04 | 0.6 | 0 | 8.28 | 43.7 | 0 | 11.3 | 26.01 | 99.42 | 11.82 | 0 | 0 | 0 | 0 | -5.62
1 | Lighting2 | 0 | 6074.41 | 0 | 227.72 | 171.66 | 0 | 6.44 | 0 | 115.27 | 0 | 222.1 | 66.67 | 52.25 | 0.09 | 19.19 | 0.6 | 0 | 8.61 | 42.8 | 0 | 11.27 | 26.01 | 99.42 | 11.82 | 0 | 0 | 0 | 0 | -5.62
2 | Lighting3 | 0 | 6364.71 | 0 | 238.6 | 171.66 | 0 | 6.44 | 0 | 120.92 | 0 | 232.98 | 66.78 | 52.25 | 0.21 | 27.77 | 0.6 | 0 | 7.96 | 45.45 | 0 | 11.4 | 26.01 | 99.42 | 11.82 | 0 | 0 | 0 | 0 | -5.62

## Datos_peoplem2perperson
run | people_m2_per_person | Gas_MWh | Elec_MWh | Gas_kWh/m2 | Elec_kWh/m2 | Boilers_MWh | Chillers_MWh | Boilers_kWh/m2 | Chillers_kWh/m2 | CE_kgCO2/m2 | UK_BER_kgCO2/m2 | EUI_kWh/m2 | Ta_max_degC | Boiler_max_kW | Chiller_max_kW | Interior_lighting_kWh/m2 | Exterior_lighting_kWh/m2 | Space_heating_(gas)_kWh/m2 | Space_heating_(elec)_kWh/m2 | Space_cooling_kWh/m2 | Pumps_kWh/m2 | Fans_interior_kWh/m2 | DHW_heating_kWh/m2 | Receptacle_equipment_kWh/m2 | Elevators_escalators_kWh/m2 | Data_center_equipment_kWh/m2 | Cooking_(gas)_kWh/m2 | Cooking_(elec)_kWh/m2 | Refrigeration_kWh/m2 | Wind_PV_kWh/m2
0 | 8.6 | 0 | 6168.15 | 0 | 231.23 | 171.66 | 0 | 6.44 | 0 | 117.09 | 0 | 225.61 | 66.71 | 52.25 | 0.13 | 22.04 | 0.6 | 0 | 8.28 | 43.7 | 0 | 11.3 | 26.01 | 99.42 | 11.82 | 0 | 0 | 0 | 0 | -5.62
1 | 17.24 | 0 | 5740.09 | 0 | 215.19 | 85.64 | 0 | 3.21 | 0 | 108.76 | 0 | 209.56 | 66.56 | 26.07 | 0 | 22.04 | 0.6 | 0 | 9.4 | 39.88 | 0 | 11.24 | 12.97 | 99.42 | 11.82 | 0 | 0 | 0 | 0 | -5.62
2 | 5.75 | 0 | 6614.07 | 0 | 247.95 | 256.72 | 0.01 | 9.62 | 0 | 125.77 | 0 | 242.33 | 66.86 | 78.15 | 0.48 | 22.04 | 0.6 | 0 | 7.83 | 47.51 | 0 | 11.53 | 38.9 | 99.42 | 11.82 | 0 | 0 | 0 | 0 | -5.62